## Info (hidden)
Contents of sheets
Sheet |  | Contents
Units |  | input of all units (VA, E, RM,DS+connection, external amps), system mode,
Units_selection |  | tables of pull-down menus
Equipment List |  | result of all necessary equipment
Units + Supplies |  | maybe deleted
temp_AMP |  | current calculation for amplifiers
Current calculation |  | pre-calculations for the VX-2000DS
RM, 24V out |  | calculations of current consumptions of RMs and 24V output
Currents |  | input sheet for all basic current consumtions being used in the other sheets
Versions
Version | Tabellenblatt | Änderungen
0.63 |  | sheets units_selction + RM, 24V out ready
0.90 |  | not done yet: surveillance interval duration setting, print layout, cell protection, Equipment List. Consideration: norm compliance indication
0.98 |  | missing: Consideration: norm compliance indication, heat dissipation
0.99 |  | DS terminal current check added, bugs in Units sheet fixed
1.00 |  | bug fixed: power factors for attention drawing signal and message were interchanged in (sheet temp_amp)
bug fixed in the power supply check for RM (sheet Units)
1.01 |  | added: check on max. output current of DS
1.02 |  | bug fixed: selection of emergency duration
1.10 |  | added:Heat Dissipation + Battery capacity (DIN VDE 0833-4 or BS 5839 p.8)
1.11 |  | translated English version to German; K46 of sheet "Geräte" modified to indicate "OK" only when text is in A46; "DIN " deleted from "DIN VDE 0833-4"; sheet "Wärmeentwicklung" unit "A" (ampere) added.
Selection of capacity standard added in sheet "Stromversorgung".
1.12 | temp_amp, temp_DS, Stromversorgung | Fehler in Kapazitätsberechnung beseitigt (keine Berücksichtigung der gewählten Norm), Erklärung zur Wärmeberechnung hinzugefügt
| Stromversorgung | Erklärung zu "Pegel" hinzugefügt
| alle | Blattschutz "ausgeblendet" aktiviert, um keine Formeln anzuzeigen
1.13 | Geräteliste | hinzugefügt: bei mehr als 3 VM-3000 Geräten muss im Modus "mit Havarieverstärker" ein VX-200PS hinzugefügt werden.
1.14 | alle | Erweiterung um 4 RM. Evtl. muss mal standby current geprüft und ggf. korrigiert werden
| temp_DS | fester Sicherheitsfaktor 1,25 ersetzt durch Verwendung von Feld $O$3, dadurch Vereinfachung der Rechnung "total"
1.15 | currents | Calculation of battery capacity of amplifiers was wrong because the calculation of D39 of this sheet was wrong because wording in cells A40-A42 was in German language
1.16 | Unit Quantities | Some comparison was made to German wording causing wrong calculation. Wording ("word") replaced by reference to names in sheet Unit_selection. Will avoid similar mistakes in future translations of the tool.
| Currents | Replaced wording with reference to sheet Unit_selection. Same reason as above.
Dropdown-Liste zur Eingabe vorgegebener Werte:
Menü Daten
Gültigkeit …
Tab Einstellungen
Zulassen: Liste
„=üb“ stellt den Bezug zum Namen üb her, hinter dem eine Liste steckt
Auf gleichem Arbeitsblatt kann der Bereich „Quelle“ markiert werden,
Namen können auf verschiedenen Arbeitsblättern verwendet werden.
Namen(sliste) erstellen
Liste markieren (ohne Überschrift; kann nach Öffnen durch Bereichswahl erfolgen)
Menü Einfügen
Namen à definieren
{Namen eingeben} [OK], verschiedene Namen können mit [Hinzufügen] hintereinander erstellt
werden, nach dem letzten mit [OK] speichern und schließen.

## Units
VM-3000 Units | [9 empty] | (delete all)
[8 empty] | VM-3000 Supplementary Tool Version | 1.16
Enter or select values in yellow fields
Results are in turquoise (blue) fields
Check
System Mode: | with standby amplifier | [6 empty] | Number of expansion units: |  | OK
Speaker Output Power |  |  | power per output
|  | ext. amplifier | Out 1 | Out 2 | Out 3 | Out 4 | Out 5 | Out 6 | total
Master Unit (VA) |  | VP-2241 | [6 empty] | 0 | Enter the output power
Expansion 1 (E1) |  | 0 | 300 | [5 empty] | 0 | Enter the output power
Expansion 2 (E2) |  | 0 | 222 | [5 empty] | 0 | Enter the output power
Expansion 3 (E3) |  | 0 | 111 | [5 empty] | 0 | Enter the output power
Expansion 4 (E4) |  | 0 | [6 empty] | 0 | Enter the output power
Expansion 5 (E5) |  | 0 | [6 empty] | 0 | Enter the output power
Expansion 6 (E6) |  | 0 | [6 empty] | 0 | Enter the output power
Expansion 7 (E7) |  | 0 | [6 empty] | 0 | Enter the output power
Expansion 8 (E8) |  | 0 | [6 empty] | 0 | Enter the output power
Expansion 9 (E9) |  | 0 | [6 empty] | 0 | Enter the output power
|  |  | max. 360 W |  | max. 120 watts per channel
Connection of VM-3000 units to power supply
VP-2000 connection to power supply
| Connect to power supply |  |  |  |  | Connect to power supply
VM-3000 unit | unit no. | terminal no. |  | VP-2000 Mod. |  | unit no. |  | terminal no. |  | Check of power supply connection
VP-2241 (VA)
Remote Microphones at VM-3000VA |  |  |  | Connect to power supply
Nr. | Model | Expansion | qty. | power source |  |  | terminal no. |  |  | Check of power supply connection
RM1
RM2
RM3
RM4
RM5
RM6
RM7
RM8
Additional Currents from VM-3000 (24V output, max. 0.3 A)
output current in [A]
VM-3000 unit | Description of consumer |  |  | permanent |  | at alarm |  | not at alarm |  | Check of power supply

## Units_selection (hidden)
NAMES
Mode
without standby amplifier
with standby amplifier
BGM/paging system
VA-Model
VM-3240VA
VM-3360VA
E-Model
VM-3240E
VM-3360E
RM
RM-200M
RM-300MF | "RM-300MF" when less than 4 units are entered
RM-Ext | Pull-down Menü einfügen:
RM-210 | 1. Bereiche der Listenwerte markieren und als Namen definieren
RM-320F | 2. Zelle f. Pull-down Menu: Gültigkeitsprüfung "Liste" wählen, im Feld "=Listenname" eintragen
DS:
VX-2000DS(1)
VX-2000DS(2)
VX-2000DS(3)
VX-2000DS(4)
VX-2000DS(5)
RM1_Connect | RM2_Connect | RM3_Connect | RM4_Connect
RM1 LINK IN | RM1 LINK IN | RM1 LINK IN | RM1 LINK IN
RM2 LINK IN | RM2 LINK IN | RM2 LINK IN | RM2 LINK IN
local power supply | local power supply | local power supply | local power supply
VX-2000DS(1) | VX-2000DS(1) | VX-2000DS(1) | VX-2000DS(1)
VX-2000DS(2) | VX-2000DS(2) | VX-2000DS(2) | VX-2000DS(2)
VX-2000DS(3) | VX-2000DS(3) | VX-2000DS(3) | VX-2000DS(3)
VX-2000DS(4) | VX-2000DS(4) | VX-2000DS(4) | VX-2000DS(4)
VX-2000DS(5) | VX-2000DS(5) | VX-2000DS(5) | VX-2000DS(5)
Terminal
1
2
3
4
5
6
Number of extensions
RM1 |  |  | RM5
0 |  |  | 0
1 |  |  | 1
2 |  |  | 2
3 |  |  | 3
| "4" when RM1 = RM-200M |  |  | "4" when RM5 = RM-200M
RM2 |  |  | RM6
0 |  |  | 0
1 |  |  | 1
2 |  |  | 2
3 |  |  | 3
| "4" when RM2 = RM-200M |  |  | "4" when RM6 = RM-200M
RM3 |  |  | RM7
0 |  |  | 0
1 |  |  | 1
2 |  |  | 2
3 |  |  | 3
| "4" when RM3 = RM-200M |  |  | "4" when RM7 = RM-200M
RM4 |  |  | RM8
0 |  |  | 0
1 |  |  | 1
2 |  |  | 2
3 |  |  | 3
| "4" when RM4 = RM-200M |  |  | "4" when RM8 = RM-200M
speaker_surveillance | Surveillance interval in AC-mains mode
100 s
4 h
24 h
AlarmPeriod
30
45
60
75
90
Standard
VDE 0833-4
BS 5839 p.8

## Unit Quantities
Quantity of Units
|  |  | VM-3000 Supplementary Tool Version | 1.16
VM-3240VA | 0
VM-3360VA | 0
VM-3240E | 0
VM-3360E | 0
VP-2241 | 1
VP-2421 | 0
VP-200VX | 1
RM-200M | 0
RM-210 | 0
RM-300MF | 0
RM-320F | 0
VX-2000DS | 0 | (according to set connections)
VX-200PS | 0
VX-2000PF | 0

## RM, 24V out (hidden)
Remote Microphones
enter here
from sheet Currents
calculated with related other sheet
calculated (from other calculation)
[8 empty] | IN1 | IN2 | IN1+IN2
VM-3000VA | [6 empty] | max. current: | 0.3 | 0.3 | 0.4
| RM-200M | RM-300MF | RM-210 | RM-320F | total | VA | power supply
RM1 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0 | 0
RM2 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0 | 0
RM3 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0 | 0
RM4 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0 | 0 | total
RM5 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0 | 0
RM6 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0 | 0
RM7 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0 | 0
RM8 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0 | 0
Sum | 0 | 0 | 0 | 0 | 0 | 0 | total I of IN1/2: | 0 | 0 | 0
max. curr. | 0.1 | 0.1 | 0.02 | 0.15 |  |  |  | 0 | 0 | 0
Max. current consumption from VM Units
| max. current: | 0.3 |  | max. total current: | 0.4
DC current
Unit |  | permanent | at EMG | not EMG | RM cur. | total at EMG | total not at EMG | DC curr. | total
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
Typical/standby current consumption from VM Units
Current per RM | [6 empty] | Current per RM from VM-3000
| RM-200M | RM-300MF | RM-210 | RM-320F | total |  | power supply | IN1 | IN2 | IN1+IN2
RM1 | 0 | 0 | 0 | 0 | 0 |  | - | 0 | 0
RM2 | 0 | 0 | 0 | 0 | 0 |  | - | 0 | 0
RM3 | 0 | 0 | 0 | 0 | 0 |  | - | 0 | 0
RM4 | 0 | 0 | 0 | 0 | 0 |  | - | 0 | 0
RM5 | 0 | 0 | 0 | 0 | 0 |  | - | 0 | 0
RM6 | 0 | 0 | 0 | 0 | 0 |  | - | 0 | 0
RM7 | 0 | 0 | 0 | 0 | 0 |  | - | 0 | 0
RM8 | 0 | 0 | 0 | 0 | 0 |  | - | 0 | 0
Sum | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0
curr. | 0.065 | 0.065 | 0.01 | 0.02
Check of RM-300MF quantity
Anz. RM-300MF |  | 0 | 0

## temp_AMP (hidden)
[5 empty] | surveillance-fact. |  | power-factor |  | sp. surv. in AC failure mode
[5 empty] | 0.0015 |  | 0.0595 |  | 4 h | [16 empty] | for calc.
[26 empty] | in temp_DS | Signal: | M, N, X
[5 empty] | AC mode |  | EMG | att-dwg. | message | [9 empty] | battery mode | [7 empty] | Standby: | L, O, V
[5 empty] | Currents for heat |  | duration | 5 | 15 | average | supply from amp |  |  |  | current consumption with RM |  |  |  | heat |  | average |  |  | current consumption w RM
[5 empty] | amp only |  | level/max | 0.70795 | 0.31623 | 0.41416 | RM |  | ext. 24V | [7 empty] | amp+int. | amp | amp+int. |  |  | 2
| model | power | power supply |  | Idle | Surv. | max. | att-dwg | mess. | att+mes | typ/Stb | max. | at EMG | no EMG | Idle all | Surv. | max. | att + mes | amp stb. | amp surv. | Stb+surv. | max. | att+mes | Stb+surv. | max+all | att+mes
VA |  | 0 | - | -- | 1.09 | 1.09 | 1.09 | 0.77166 | 0.34469 | 0.45143 | 0 | [7 empty] | 0.62 | 0.62 |  | 0.62 | 0.25678 |  | 0.62 | 0.25678
E1 |  | 0 | - | --
E2 |  | 0 | - | --
E3 |  | 0 | - | --
E4 |  | 0 | - | --
E5 |  | 0 | - | --
E6 |  | 0 | - | --
E7 |  | 0 | - | --
E8 |  | 0 | - | --
E9 |  | 0 | - | --
VA | VP-2241 | 0 | - | VP-2241-- | 0.47 | 0.47 | 0.47 | 0.33273 | 0.14863 | 0.19465 |  |  |  |  | 0.47 | 0.47 | 0.47 | 0.19465 | 0.033 | 0.32229 | 0.033 | 0.47 | 0.19465 | 0.033 | 0.47 | 0.033
E1 | 0 | 0 | - | 0--
E2 | 0 | 0 | - | 0--
E3 | 0 | 0 | - | 0--
E4 | 0 | 0 | - | 0--
E5 | 0 | 0 | - | 0--
E6 | 0 | 0 | - | 0--
E7 | 0 | 0 | - | 0--
E8 | 0 | 0 | - | 0--
E9 | 0 | 0 | - | 0--
VA-RM1 | 0 | 0 | - | 0-- | 0 | [11 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VA-RM2 | 0 | 0 | - | 0-- | 0 | [11 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VA-RM3 | 0 | 0 | - | 0-- | 0 | [11 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VA-RM4 | 0 | 0 | - | 0-- | 0 | [11 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VA-RM5 | 0 | 0 | - | 0-- | 0 | [11 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VA-RM6 | 0 | 0 | - | 0-- | 0 | [11 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VA-RM7 | 0 | 0 | - | 0-- | 0 | [11 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VA-RM8 | 0 | 0 | - | 0-- | 0 | [11 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | no.o.ext. |  | 1: w/o stb
|  |  | VM-3360 | 2: w stb | 2 | 0.95 | 36.1 | 24A | 28
|  |  | VM-3240 | 3: BGM/p. |  | 0.8 | 36.1 | 18A | 28

## temp_DS (hidden)
[7 empty] | standby duration [h] | 24 | [5 empty] | 1.25
[7 empty] | EMG duration [min] | 30 | de-rating f. | 1 | de-r. x dur. | 0.5 | safety: | 1
| VM-3240 |  | VM-3360 |  |  | VP- |  | bat | bat |  | bat |  | Single capacity requirement |  |  | max. I
| VA | E | VA | E | RM | 2241 | 2421 | stb_cur | EMG cur. | output | currents | capacity | standby | EMG | total
VX-2000DS(1)-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | standby | standby | 0 | 0 | 0 | 0
VX-2000DS(1)-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VX-2000DS(1)-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EMG | EMG | 0 | 0 | 0 | 0
VX-2000DS(1)-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VX-2000DS(1)-5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | total | 0 | 0 | 0 | 0
VX-2000DS(1)-6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
VX-2000DS(2)-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | standby | standby | 0 | 0 | 0 | 0
VX-2000DS(2)-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VX-2000DS(2)-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EMG | EMG | 0 | 0 | 0 | 0
VX-2000DS(2)-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VX-2000DS(2)-5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | total | 0 | 0 | 0 | 0
VX-2000DS(2)-6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
VX-2000DS(3)-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | standby | standby | 0 | 0 | 0 | 0
VX-2000DS(3)-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VX-2000DS(3)-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EMG | EMG | 0 | 0 | 0 | 0
VX-2000DS(3)-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VX-2000DS(3)-5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | total | 0 | 0 | 0 | 0
VX-2000DS(3)-6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
VX-2000DS(4)-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | standby | standby | 0 | 0 | 0 | 0
VX-2000DS(4)-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VX-2000DS(4)-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EMG | EMG | 0 | 0 | 0 | 0
VX-2000DS(4)-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VX-2000DS(4)-5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | total | 0 | 0 | 0 | 0
VX-2000DS(4)-6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
VX-2000DS(5)-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | standby | standby | 0 | 0 | 0 | 0
VX-2000DS(5)-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VX-2000DS(5)-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EMG | EMG | 0 | 0 | 0 | 0
VX-2000DS(5)-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VX-2000DS(5)-5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | total | 0 | 0 | 0 | 0
VX-2000DS(5)-6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q
[11 empty] | DS(1) | 0
Intervals speaker line surveillance in battery backup mode: | [10 empty] | DS(2) | 0
100 s | [10 empty] | DS(3) | 0
4 h | [10 empty] | DS(4) | 0
24 h | [10 empty] | DS(5) | 0
[11 empty] | Anz. DS | 0
WENN('Power Supply'!$E$5="BS 5839 p.8";M10+M8;
WENN(UND('Power Supply'!$E$5="VDE 0833-4";'Power Supply'!$B$4>=24);temp_DS!$I$2*temp_DS!L8+temp_DS!L10*temp_DS!$I$3/60;
WENN(UND('Power Supply'!$E$5="VDE 0833-4";'Power Supply'!$B$4<24);1,25*(temp_DS!$I$2*temp_DS!L8+temp_DS!L10*temp_DS!$I$3/60))))

## Power Supply
Power Supply Check and Battery Capacities
[11 empty] | VM-3000 Supplementary Tool Version: | 1.16
Duration of mains power loss |  |  | Surveillance interval at mains power loss |  |  |  |  | Duration of emergency broadcast
Standby duration | 24 | hours |  | Interval | 4 h |  | Message |  | duration | 15 | level | -10
alarm duration | 30 | min. |  |  |  |  | Att.drw.sig. |  | duration | 5 | level | -3
Level: average output level relative to rated power
Applied standard for capacity calculation: | [5 empty] | VDE 0833-4
|  | VM-3240 |  | VM-3360 |  | VP- |  |  | single capacities |  | battery |  | terminal
VX-2000DS | Terminal | VA | E | VA | E | 2241 | 2421 | RM | standby | alarm | capacity |  | current check
VX-2000DS(1) | 1 | [11 empty] | OK
| 2 | [11 empty] | OK
| 3 | [11 empty] | OK
| 4 | [11 empty] | OK
| 5 | [11 empty] | OK
| 6 | [11 empty] | OK
VX-2000DS(2) | 1 | [11 empty] | OK
| 2 | [11 empty] | OK
| 3 | [11 empty] | OK
| 4 | [11 empty] | OK
| 5 | [11 empty] | OK
| 6 | [11 empty] | OK
VX-2000DS(3) | 1 | [11 empty] | OK
| 2 | [11 empty] | OK
| 3 | [11 empty] | OK
| 4 | [11 empty] | OK
| 5 | [11 empty] | OK
| 6 | [11 empty] | OK
VX-2000DS(4) | 1 | [11 empty] | OK
| 2 | [11 empty] | OK
| 3 | [11 empty] | OK
| 4 | [11 empty] | OK
| 5 | [11 empty] | OK
| 6 | [11 empty] | OK
VX-2000DS(5) | 1 | [11 empty] | OK
| 2 | [11 empty] | OK
| 3 | [11 empty] | OK
| 4 | [11 empty] | OK
| 5 | [11 empty] | OK
| 6 | [11 empty] | OK
Calculation of battery capacity
VDE 0833-4: | ≥ 24 h: |  | C = t1 x I1 + t2 x I2
| < 24 h: |  | C = 1,25 x (t1 x I1 + t2 x I2)
BS 5839 p.8: |  |  | C = 1,25 x (t1 x I1 + d x t2 x I2)
|  |  | t1: | standby duration |  |  |  | I1: | current consumption at standby
|  |  | t2: | alarm duration |  |  |  | I2: | current consumption at alarm
|  |  | d: | capacity de-rating of battery

## Heat Dissipation
Heat Dissipation | [5 empty] | Application of this table
|  |  |  | VM-3000 Supplementary Tool Version: | 1.16
AC-mains operation | Unit/Consumption | no audio | BGM + page | alarm | maximum | The heat calculation of each single VX-2000DS allows the distribution of the system into different locations. Then the heat dissipation of the VX-2000DS in that location must just be added.
VX-2000DS-1 | heat [kcal/h] | 0 | 0 | 0 | 0
| heat [kJ/h] | 0 | 0 | 0 | 0
| heat [W] [J/s] | 0 | 0 | 0 | 0
| heat [BTU/h] | 0 | 0 | 0 | 0
| AC-mains current | 0 | 0 | 0 | 0
| AC-mains power | 0 | 0 | 0 | 0 | When using additional equipment like CD players, then you must add their effective (real) power to the AC-mains wattage for the location where the equipment is installed.
VX-2000DS-2 | heat [kcal/h] | 0 | 0 | 0 | 0
| heat [kJ/h] | 0 | 0 | 0 | 0
| heat [W] [J/s] | 0 | 0 | 0 | 0
| heat [BTU/h] | 0 | 0 | 0 | 0
| AC-mains current | 0 | 0 | 0 | 0 | "Wattage AC mains" means the effective power from AC- mains. The apparent power can easily be calculated just by multiplying the "current AC-mains" with the AC-mains voltage.
| AC-mains power | 0 | 0 | 0 | 0
VX-2000DS-3 | heat [kcal/h] | 0 | 0 | 0 | 0
| heat [kJ/h] | 0 | 0 | 0 | 0
| heat [W] [J/s] | 0 | 0 | 0 | 0
| heat [BTU/h] | 0 | 0 | 0 | 0
| AC-mains current | 0 | 0 | 0 | 0
| AC-mains power | 0 | 0 | 0 | 0 | Remarks on Tolerances
VX-2000DS-4 | heat [kcal/h] | 0 | 0 | 0 | 0
| heat [kJ/h] | 0 | 0 | 0 | 0 | The heat and power values
| heat [W] [J/s] | 0 | 0 | 0 | 0 | are calculated with an
| heat [BTU/h] | 0 | 0 | 0 | 0 | AC-mains voltage of 230 V AC.
| AC-mains current | 0 | 0 | 0 | 0 | In case of a higher or lower
| AC-mains power | 0 | 0 | 0 | 0 | AC-mains voltage, the values
VX-2000DS-5 | heat [kcal/h] | 0 | 0 | 0 | 0 | change similar as the
| heat [kJ/h] | 0 | 0 | 0 | 0 | AC-mains voltage. I.e. when
| heat [W] [J/s] | 0 | 0 | 0 | 0 | the AC-mains voltage is 5%
| heat [BTU/h] | 0 | 0 | 0 | 0 | up, then the heat distribution,
| AC-mains current | 0 | 0 | 0 | 0 | power consumption and
| AC-mains power | 0 | 0 | 0 | 0 | current consumption is also
increased by approximately
TOTAL (AC mains) | Output | no audio | BGM + page | alarm | maximum | 5%.
| heat [kcal/h] | 0 | 0 | 0 | 0
| heat [kJ/h] | 0 | 0 | 0 | 0 | In continental Europe the
| heat [W] [J/s] | 0 | 0 | 0 | 0 | AC-mains voltage has a
| heat [BTU/h] | 0 | 0 | 0 | 0 | tolerance of ±10%, so for a
| AC-mains current | 0 | 0 | 0 | 0 | secure heat dissipation
| AC-mains power | 0 | 0 | 0 | 0 | 10% can be added.
Explanation
no audio: | no BGM, pageing, e.g. pure voice alarm system
BGM + page: | operation with background music and paging
alarm: | emergency mode according to entered values
maximum: | maximum values that occur only very shortly, for planning fuses
Since the maximum heat dissipation is theoretically only, it is shaded

## Heat Dis. Hilfstabellen (hidden)
Hilfsfunktion für Cosinus phi:
[11 empty] | Messergebnisse. Netzbetrieb, nichts angeschlossen | [7 empty] | Liste für Auswahl
1. Messung | P=40W | 2.Messund | P=200 bis 350 W |  | 40 | 359 |  |  |  |  | VM-3360VA: 40 Watt | [7 empty] | DIN VDE 0833-4
| S=59,7VA |  | S= bis 480 VA |  | 0.67 | 0.77 |  |  |  |  | VM-3240VA: 40 Watt | [7 empty] | BS 5839 p.8
| U=230V |  | U=230V | [7 empty] | VM-3360E: 35 Watt
| cos phi= 0,67 |  | cos phi=0,77 | [7 empty] | VM-3240E: 35 Watt
Eine kleine Hilfe
100V -> 0dB
31,6V -> -10dB
10V -> -20dB
3,16V -> -30dB
Lineare Abhängigkeit
Sinus-Signal: 200Hz, 0dB (100V)
[11 empty] | 30 | 60 | 90 | 120 | 150 | 180 | 210 | 240 | 270 | 300 | 330 | 360
[11 empty] | 114 | 185 | 251 | 320 | 385 | 454 | 521.807 | 589.508 | 657.209 | 724.91 | 792.611 | 860.312
Wirkungsgrad
Hilfsfunktion für die Berchnung der aufgenommenen Leistung in BGM+Pagging:
120 | 240
54 | 61
Sinus-Signal: 200Hz, -10dB (31,6V)
[11 empty] | 30 | 60 | 90 | 120 | 150 | 180 | 210 | 240 | 270 | 300 | 330 | 360
[11 empty] | 60 | 71 | 100 | 119 | 140 | 160.394 | 181.193 | 201.992 | 222.791 | 243.59 | 264.389 | 285.188
Hilfstabelle für die Zuordnung der angeschlossenen Lautsprecherleistung zu den VX-2000DS
VX-2000DS(1) | VX-2000DS(2) | VX-2000DS(3) | VX-2000DS(4) | VX-2000DS(5)
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | Aufgenommene Leistung aus dem Netz | [5 empty] | Sinus-Signal: 200Hz, -20dB(10V)
0 | 0 | 0 | 0 | 0 | Angeschlossene Gesamtlautsprecherleistung | [5 empty] | 30 | 60 | 90 | 120 | 150 | 180 | 210 | 240 | 270 | 300 | 330 | 360
[11 empty] | 40 | 46.1 | 48 | 54 | 58 | 62.384 | 66.773 | 71.162 | 75.551 | 79.94 | 84.329 | 88.718
Abgegebene Wärme in Watt
0 | 0 | 0 | 0 | 0
Hilfsfunktion dB und Spannung. (Die Spannung am Lautsprecher direkt)
| -30 | -20 | -10 | -5 | -3 | 0
| 3.16 | 10 | 31.6 | 56 | 70.5 | 100
Sinus-Signal: 200Hz, -30dB(3,16V)
[11 empty] | 30 | 60 | 90 | 120 | 150 | 180 | 210 | 240 | 270 | 300 | 330 | 360
[11 empty] | 40 | 42 | 44 | 45 | 48 | 49.494 | 51.393 | 53.292 | 55.191 | 57.09 | 58.989 | 60.888
Hilfsfunktion für abgegebene Wärme pro Watt ( Nicht im Schrank, sondern irgendwo draußen)
0 | -3 | -5 | -10 | -20
1 | 0.5 | 0.32 | 0.1 | 0.001
[11 empty] | Hilfsfunktion: Steigung der Funktionen/Pegel |  |  |  | -30 | -20 | -10 | 0 | Pegel in dB |  |  |  |  | Hilfsfunktion: Spannung/Pegel | -30 | -20 | -10 | 0 | Spannung in V
[11 empty] | (siehe oben die Funktionen, y=Steigung*x +b) |  |  |  | 0.0633 | 0.1463 | 0.6933 | 2.2567 | Steigung der obigen Funktionen | [5 empty] | 3.16 | 10 | 31.6 | 100
Diese Leistung geht an den Lautprechern verloren
Pro Watt der angeschlossenen Lautsprecherleistung, abgegebene Wärme im Notfall (Ist abhängig vom Pegel und Zeit)
VX-2000DS(1) | VX-2000DS(2) | VX-2000DS(3) | VX-2000DS(4) | VX-2000DS(5) |  |  | 0.20059
0 | 0 | 0 | 0 | 0
Maximum der abgegebenen Wärme, also bei 0 dB | [7 empty] | Zuordnung der angeschlossenen Lautsprecherleistung
VX-2000DS(1) | VX-2000DS(2) | VX-2000DS(3) | VX-2000DS(4) | VX-2000DS(5) |  |  |  | VX-2000DS(1) | VX-2000DS(2) | VX-2000DS(3) | VX-2000DS(4) | VX-2000DS(5)
0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | Aufgenommene Leistung aus dem Netz |  |  | 0 | 0 | 0 | 0 | 0 | Wärme an den Lautsprechern bei 0dB (100V)
0 | 0 | 0 | 0 | 0 | Wärme die an den Lautsprechern entsteht
0 | 0 | 0 | 0 | 0 | Entstehende Wärme in Watt
Hilfstabelle für die Aufgenomme Leistung aus dem Netz bei EMG (also 2 Pegel: Messege+Aufmerksamkeitssignal | [5 empty] | Allgemeine Funktion für die aufgenommene Leistung: | [7 empty] | Funktion pro Watt angeschlossener Lautsprecheleistung, abgegebene Wärme in Abhängigkeit vom Pegel
[6 empty] | y=2,2567*exp(0,1228*x)+40 | [7 empty] | y=exp(0,23*x)
VX-2000DS(1) | VX-2000DS(2) | VX-2000DS(3) | VX-2000DS(4) | VX-2000DS(5) |  |  |  | VX-2000DS(1) | VX-2000DS(2) | VX-2000DS(3) | VX-2000DS(4) | VX-2000DS(5)
40 | 40 | 40 | 40 | 40 |  |  |  | 0 | 0 | 0 | 0 | 0 |  | Kombinierte Funktion aus Messege und Aufmerksamkeitssignal gewichtet nach der Zeit
40 | 40 | 40 | 40 | 40 |  |  |  | 0 | 0 | 0 | 0 | 0 |  | y=exp(0,23*x)*Message/(Message+Aufmerksamkeit)+exp(0,23*x)*Aufmerksamkeit*(Message+Aufmerksamkeit)
40 | 40 | 40 | 40 | 40 |  |  |  | 0 | 0 | 0 | 0 | 0
40 | 40 | 40 | 40 | 40 |  | gleiche Tabelle ohne 40 -> |  | 0 | 0 | 0 | 0 | 0
40 | 40 | 40 | 40 | 40 |  |  |  | 0 | 0 | 0 | 0 | 0 |  | Entstehende Wärme im Schrank
40 | 40 | 40 | 40 | 40 |  |  |  | 0 | 0 | 0 | 0 | 0
40 | 40 | 40 | 40 | 40 |  |  |  | 0 | 0 | 0 | 0 | 0
40 | 40 | 40 | 40 | 40 |  |  |  | 0 | 0 | 0 | 0 | 0
40 | 40 | 40 | 40 | 40 |  |  |  | 0 | 0 | 0 | 0 | 0 |  | VX-2000DS(1) | VX-2000DS(2) | VX-2000DS(3) | VX-2000DS(4) | VX-2000DS(5)
40 | 40 | 40 | 40 | 40 |  |  |  | 0 | 0 | 0 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | Aus dem Netz aufgenommene Leistung | 0 | 0 | 0 | 0 | 0

## Currents (hidden)
Currents | B | C | D | E | F | G | H | I | J | K | L | M | N | O
|  | out max. | [7 empty] | AC-m. idle (35V) |  | Battery (24V)
| Idle AC | ext | max | out pwr | Amp | A/W | P DC | P AC | loss AC | no load | load 178W | idle low | idle surv. | delta
VM-3240VA | 0.8 | 0.4 | 18 | 240 | 16.8 | 0.07 | 504 | 600 | 96 | 0.8 | 0.83 | 0.62 | 0.89 | 0.27 | 4
VM-3240E | 0.76 | 0.4 | 18 | 240 | 16.84 | 0.070167 | 504 | 600 | 96 | 0.76 | 0.79 | 0.58 | 0.85 | 0.27 | 5
VM-3360VA | 1.09 | 0.4 | 24 | 360 | 22.51 | 0.062528 | 672 | 850 | 178 | 1.09 | 1.02 | 0.62 | 1.05 | 0.43 | 6
VM-3360E | 1.06 | 0.4 | 24 | 360 | 22.54 | 0.062611 | 672 | 850 | 178 | 1.06 | 1.02 | 0.58 | 1.01 | 0.43 | 7
| max. | typ/Stb
RM-200M | 0.1 | 0.065 | [12 empty] | 9
RM-210 | 0.02 | 0.01 | [12 empty] | 10
RM-300MF | 0.1 | 0.065 | [12 empty] | 11
RM-320F | 0.15 | 0.02 | [12 empty] | 12
| Idle AC | stb | idle bat. | max | out pwr
VP-2241 | 0.47 | 0.033 | 0.32229 |  | 240 | [9 empty] | 15
VP-2421 | 0.82 | 0.033 | 0.56229 |  | 360 | [9 empty] | 16
max. currents [A]
RM1 LINK | 0.3 | [13 empty] | 19
RM2 LINK | 0.3 | [13 empty] | 20
+24V OUT | 0.3 | [13 empty] | 21
all together | 0.4 | [13 empty] | 22
Standby mode |  |  | VM | VP | VM | VP | VM | VP
duration surveillance |  |  | 40 | 10 | 40 | 10 | 40 | 10
duration w/o surveillance |  |  | 90 | 90 | 9560 | 9590 | 57560 | 57590
|  |  | 100 s |  | 4 h |  | 24 h
Battery de-rating factors
Alarm period
| T2 | D2
| 30 | 1.9
| 45 | 1.7
| 60 | 1.6
| 75 | 1.5
| 90 | 1.45
System mode |  |  | 2
without standby amplifier |  |  | 1
with standby amplifier |  |  | 2
BGM/paging system |  |  | 3